ifc@islipflowcontrols.com

1145 Sutton Dr., Unit #3				P.O. Box 2989		        	Tel.: 905-335-8777 Fax: 905-335-0977

Burlington, ON, Canada				Buffalo, NY		         	Toll Free Tel.: 1-866-872-0072

L7L 5Z8						14240-2989 		         	Toll Free Fax: 1-866-872-0073

GENERAL OPERATION OF THE IFC

# EXTERNAL BACKWASH FEATURE

The configuration of the IFC Model A150FSBW strainer with the external backwash feature is very similar to the standard design. With this external backwash feature the strainer incorporates an external backwash arm, which rotates in sync with the internal backwash arm. The external pressurized backwash water is introduced into the strainer and is channeled through the rotating external backwash arm and the associated spray nozzles. The spray nozzles are directed at the strainer screen and the internal backwash arm. Since the external backwash fluid is pressurized above the strainer line pressure (Recommended minimum 20 psig above) any strainer particles that are trapped in the strainer screen are dislodged and removed through the internal backwash arm. The attached drawing shows the basis set-up of the strainer configuration.

The external backwash feature is used when the strainer line pressure in combination with any backwash line losses would not be suitable to remove effectively particles that are trapped on the strainer screen during backwashing (i.e Strainer line pressure under 15 psig). The external backwash feature IFC offers can significantly increase the efficiency of the strainer backwashing process.